# WIT 8K-HU — Cannot enable AC (grid) charging via VPP Modbus registers

Inverter: Growatt WIT 8K-HU (DTC: 5603) VPP Protocol Version: 202 (V2.02) Firmware: YE1.0 Connection: Modbus TCP (port 502)

## Problem

I use VPP registers to remotely control battery modes (charge, discharge, hold) for energy price optimization. All modes work correctly except grid charging via remote power control (30407-30409) — the inverter rejects the register value needed to enable AC charging.

## What works

| Operation | Registers | Result |
| --- | --- | --- |
| Discharge to load/grid | 30407=1, 30409=-100 | Works — battery discharges at full power |
| Hold (idle) | 30407=1, 30409=0 | Works — battery holds SOC |
| TOU schedule (positive power) | 30411=N, 30412-30414 periods | Works — charges from grid even without PV |
| AC charge enable = PV priority | 30410=1 (via FC 0x10) | Accepted |

## What does NOT work

Register 30410 = 2 (AC priority) — needed to enable grid charging via remote power control (30407/30409):

Write FC 0x06: address=30410, value=2
Response: ExceptionResponse(function_code=134, exception_code=1)  — Illegal Function

The register only accepts values 0 (disabled) and 1 (PV priority). Value 2 (AC priority) is rejected by the v2.02 firmware.

With 30410=1 and remote power control (30407=1, 30409=+100), the inverter does not charge from the grid. The duration register (30408) does not count down, suggesting the remote charge command is not being executed.

I also tried:

- Legacy register 949 (ac_charge_enable) — write succeeds but value does not persist (reads back 0)

- Legacy register 905 (ac_charge_power_rate) — same behavior, writes accepted but not retained

- Legacy registers 201/202 (work mode + power rate) — register 201 does not persist

## Current workaround

I use TOU schedule periods (30411-30414) with positive power values (+100%) instead of remote power control (30407-30409) for charging. This works, but TOU scheduling is less flexible than remote power control — it requires rewriting period registers for each mode change

## Questions

- Is there a different register or register sequence on the WIT platform that enables AC/grid charging via remote power control (30407-30409)?

- Is 30410=2 support planned for a future firmware update? Or do I need to upgrade inverter hardware?

- Is there an alternative VPP command to achieve grid charging without TOU periods?